Annexure-B

Specification for Sinking of Tube Well of size 100 mm x 50 mm at a depth 335m and installation of submersible pump mortor set, in favour TAMLUK-GHATAL CENTRAL CO-OPERATIVE BANK, HALDIA, PURBA MEDINIPUR. -USE OF PVC PIPE -SKIPPER / ORIPLAST

| SL No | Reference | DescriptionofItem | Unit | Qty. |
| --- | --- | --- | --- | --- |
| 1 | sec(A)-(V)Sl.no.- 1(d)(i)&(ii)ofS&Pw, Pg-49&1(f)(i)ofPg- 50 | Labour for boring tubewell of required dia. By water jet system through any type of soil strata including hire and labour charges for boring pipes, scaffolding, tools and plants as necessary and taking out them and lowering pipes, strainers, blind pipe etc. and fitting and fixing the same complete including bucket was hing and other incidental works in the connection. The tube well should have a minimum 50 mm gap in between the outside of the tubewell pipe and the bore .For depth upto 150 metre for 50 mm dia. tube well with top enlargement of 100mmdia. |  |  |
|  |  | (i)50mm dia. Boring etc.(upto150mfrom GL) | m | 70.00 |
|  |  | (ii)50mmdia.boringetc.(below150mfromGL) | m | 185.00 |
|  |  | (iii)100mmdia.boringetc.topenlargement | m | 80.00 |
| 2 | sec(A)-(II)Sl.no.- 19(III)(A)ofS&Pw, pg-13 | Supply of PVC pipes & fittings (medium duty) conforming to ASTMD-1785andthreadedtomatchwithGIPipesasperIS: 1239 (Part - I). |  |  |
|  |  | (i)100mmdiapipe | m | 80.00 |
|  |  | (ii)50mmdiapipe | m | 235.00 |
| 3 | sec(A)-(V)Sl.no.- 6(ii)ofS&Pw,Pg-52 | Supplying50mmdiaPVCstrainerofapprovedmakewith adapter conforming to I.S.12818 specifications. | m | 20.00 |
| 4 | sec(A)-(V)Sl.no.- 9(ii)ofS&Pw,pg-53 | Supplying,fittingandfixing50mmdiasteelcutterpieceupto 450 mm long with socket. | each | 1.00 |
| 5 | sec(A)-(V)Sl.no.- 10(ii)ofS&Pw,pg-53 | Supplying, fitting and fixing plug of approved make conforming to I.S. specification. | each | 1.00 |
| 6 | sec(A)-(V)Sl.no.- 17(i)ofS&Pw,pg-54 | Supplying,fittingandfixing100mmx50mmheavytypebell mouth reducing socket. | each | 1.00 |
| 7 | sec(A)-(V)Sl.no.- 18(i)ofS&Pw,pg-54 | Supplying,fittingandfixing100mmdiaG.I.capattop. | each | 1.00 |
| 9 | sec(A)-(V)Sl.no.-20 of S&Pw, pg -55 | Washing and developing tube well with air compressor pump andenginefor8(eight) hours continuous pumping per daywith necessary arrangements for testing the yield in gallons per hour with 'V' notch including hire and labour charges for all tools and plants and scaffolding as required. | day | 1.00 |
| 10 | sec(A)-(V)Sl.no.-24 of S&Pw, pg-55 | Packing the annular space between the outside of the tubewell pipes & strainers and the bore with pea size washed gravel of approved quality having size from 2 mm to 5 mm or the size approved by the Engineer in-charge including cost of all materials labour and equipment complete. | cum | 1.00 |
| 11 | sec(A)-(VI)Sl.no.-23 of S&Pw, pg-55 | Collecting sample of water for bacteriological and chemical test from any depth at any time during execution of work including hire and labour charges for tools and plants and sterilising the equipments, paying all charges and fees, testing etc. complete in all respect as per direction. | cum | 1.00 |

| SL No | Reference | DescriptionofItem | Unit | Qty. |
| --- | --- | --- | --- | --- |
| 12 | Pg-8,Sl.No-6 WRIDD | Charges for mobilisation of drilling equipments, tools & plants etc and transportation of departmental materials fromsub- divisional store to work site and returning excess departmental materials if any, to sub divisional store after completion of work . | each tube well | 1 |
| 13 | Marketrate | Supplying of 2HPmultistageSubmersiblepumpmortorsetat 42 m head with DLO starter. The motor shall be designed for operation at 240 V (±10 % ) , single phase 50 cycle per second (± 5 %) , AC supply with 3 mtrs flat water proof cable ofsize1.5sqmm .The motor shall be ISI marked.Thepump with multi stage with strainer, non return valve having 1.5 '' discharge outlet duly with ISI marked . | each | 1.00 |
| 14 | Marketrate | Supplyof3 crore 1.5 sq mm Flat Weather Proof Copper PVC insulated heavy duty cable as per IS 694/1990 with latest amendments. | m | 60.00 |
| 15 | Marketrate | Supply40 mm dia (33Kg/sqm pressure)PVC column pipe Each3m long. | each | 14.00 |
| 16 | Pg-27, Sl. No- 5.1(b)(ii)ofWRIDD | Installation of submersible electro motor pumping set by using necessary requisite, tools and plants by lowering the same within the tubewell housing pipe upto the following depth as per direction by fitting, fixing column pipes and other accessories,-----etc complete. | each | 1.00 |
| 17 | G-1,Slno-2(a)of PWD (E) | Earthingwith50mm diapipe3.64mmthickx3.04m long and 1x 4 SWG G.I. wire (4 mts. Long) 13 mm dia. × 80 mm long G.I. bolts, doublenuts, double washers including supplying andfixing15mm.diaG.I.Pipeprotection(1mt.long)to be filled with bitumen, partly under the ground level and partly above the ground level, driven to an average depth of 3.65 metre(12')below the ground level and restoring the surface duly rammed for soft soil. ByISI - Medium GI pipe. (TATA) | Per set | 1 |
| 18 | Pg-12, Sl. No- 19(I)ofPWD(S&P) | Supplying, fitting and fixing PVC pipes of approved make of Schedule80(medium duty)conformingtoASTMD-1785and threadedtomatchwithGIPipesasperIS:1239(Part-I).with all necessary accessories, specials viz. socket, bend, tee, union ,cross, elbo,nipple ,longscrew, reducing socket ,reducing tee, short piece etc. fitted with holder bats clamps, including cutting pipes, making threads, fitting, fixing etc.complete in all respect including cost of all necessary fittings as required,jointing materials and two coats of painting with approved paint in any position above ground. (a) For Exposed Work v) 50 mm dia PVC Pipes. | mtr | 20 |