Technical Bid										Annexure-II

Specification for Sinking of Tube Well of size 100 mm x 50 mm at a depth 250 m and installation of submersible pump motor set, in favour TAMLUK-GHATAL CENTRAL CO-OPERATIVE BANK,

| TAMLUK/ HALDIA,PURBA MEDINIPUR.-USE OF PVC PIPE -SKIPPER / ORIPLAST SL No | Reference | Description of Item | Vendor Comments |
| --- | --- | --- | --- |
| 1 | sec(A)-(V)Sl.no.- 1(d)(i)&(ii)of S&Pw, Pg-49 & 1(f)(i) of Pg- 50 | Labour for boring tube well of required dia. by water jet system through any type of soil strata including hire and labour charges for boring pipes,scaffolding, tools and plants as necessary and taking out them and lowering pipes, strainers, blind pipe etc. and fitting and fixing the same complete including bucket washing and other incidental works in the connection. The tube well should have a minimum 50 mm gap in between the outside of the tubewell pipe and the bore.For depth upto 150 metre for 50 mm dia. tube well with top enlargement of 100 mm dia. |  |
|  |  | (i) 50 mm dia. boring etc.(upto 150 m from GL) |  |
|  |  | (ii) 50 mm dia. boring etc.(below 150 m from GL) |  |
|  |  | (iii) 100 mm dia. boring etc. top enlargement |  |
| 2 | sec(A)-(II)Sl.no.- 19(III)(A) of S&Pw, pg-13 | Supply of PVC pipes & fittings (medium duty) conforming to ASTMD -1785 and threaded to match with GI Pipes as per IS : 1239 (Part - I). |  |
|  |  | (i) 100 mm dia pipe |  |
|  |  | (ii) 50 mm dia pipe |  |
| 3 | sec(A)-(V)Sl.no.- 6(ii)of S&Pw, Pg-52 | Supplying 50 mm dia PVC strainer of approved make with adapter conforming to I.S.12818 specifications. |  |
| 4 | sec(A)-(V)Sl.no.- 9(ii)of S&Pw,pg-53 | Supplying, fitting and fixing 50 mm dia steel cutter piece upto 450 mm long with socket. |  |
| 5 | sec(A)-(V)Sl.no.- 10(ii)of S&Pw, pg-53 | Supplying, fitting and fixing plug of approved make conforming to I.S. specification. |  |
| 6 | sec(A)-(V)Sl.no.- 17(i)of S&Pw,pg-54 | Supplying, fitting and fixing 100 mm x 50 mm heavy type bell mouth reducing socket. |  |
| 7 | sec(A)-(V)Sl.no.- 18(i)of S&Pw,pg-54 | Supplying, fitting and fixing 100 mm dia G.I. cap at top. |  |
| 9 | sec(A)-(V)Sl.no.- 20 of S&Pw, pg -55 | Washing and developing tube well with air compressor pump and engine for 8 (eight) hours continuous pumping per day with necessary arrangements for testing the yield in gallons per hour with 'V' notch including hire and labour charges for all tools and plants and scaffolding as required. |  |
| 10 | sec(A)-(V)Sl.no.- 24 of S&Pw, pg-55 | Packing the annular space between the outside of the tube well pipes & strainers and the bore with pea size washed gravel of approved quality having size from 2 mm to 5 mm or the size approved by the Engineer-incharge including cost of all materials labour and equipment complete. |  |
| 11 | sec(A)-(VI)Sl.no.- 23 of S&Pw, pg-55 | Collecting sample of water for bacteriological and chemical test from any depth at any time during execution of work including hire and labour charges for tools and plants and sterilising the equipments, paying all charges and fees, testing etc. complete in all respect as per direction. |  |

| SL No | Reference | Description of Item | Vendor comments |
| --- | --- | --- | --- |
| 12 | Pg-8, Sl. No-6 WRIDD | Charges for mobilisation of drilling equipments, tools & plants etc and transportation of departmental materials from sub- divisional store to work site and returning excess departmental materials if any, to sub divisional store after completion of work . |  |
| 13 | Market rate | Supplying of 2 HP multi stage Submersible pump mortor set at 42 m head with DLO starter. The motor shall be designed for operation at 240 V (±10 % ) , single phase 50 cycle per second (± 5 %) , AC supply with 3 mtrs flat water proof cable of size 1.5 sq mm . The motor shall be ISI marked . The pump with multi stage with strainer, non return valve having 1.5 '' discharge outlet duly with ISI marked . |  |
| 14 | Market rate | Supply of 3 crore 1.5 sq mm Flat Weather Proof Copper PVC insulated heavy duty cable as per IS 694/1990 with latest amendments. |  |
| 15 | Market rate | Supply 40 mm dia (33Kg/sqm pressure ) PVC column pipe Each 3m long. |  |
| 16 | Pg-27, Sl. No- 5.1(b)(ii) of WRIDD | Instalation of submersible electro motor pumping set by using necessary requisite, tools and plants by lowering the same within the tubewell housing pipe upto the following depth as per direction by fitting, fixing column pipes and other accessories,--- -- etc complete. |  |
| 17 | G-1, Sl no-2(a) of PWD (E) | Earthing with 50 mm dia pipe 3.64 mm thick x 3.04 m long and 1x 4 SWG G.I. wire (4 mts. Long) 13 mm dia. × 80 mm long G.I. bolts, double nuts , double washers including supplying and fixing 15 mm. dia G.I. Pipe protection (1 mt. long) to be filled with bitumen, partly under the ground level and partly above the ground level, driven to an average depth of 3.65 metre(12') below the ground level and restoring the surface duly rammed for soft soil. By ISI - Medium GI pipe. (TATA) |  |
| 18 | Pg-12, Sl. No- 19(I) of PWD (S & P) | Supplying, fitting and fixing PVC pipes of approved make of Schedule 80 (medium duty) conforming to ASTMD - 1785 and threaded to match with GI Pipes as per IS : 1239 (Part - I). with all necessary accessories, specials viz. socket, bend, tee, union, cross, elbo, nipple, long screw, reducing socket, reducing tee, short piece etc. fitted with holder bats clamps, including cutting pipes, making threads, fitting, fixing etc.complete in all respect including cost of all necessary fittings as required,jointing materials and two coats of painting with approved paintin any position above ground. (a) For Exposed Work v) 50 mm dia PVC Pipes. |  |

Signature of Bidder with seal

Signature of Bidder with seal